| Functional specification |
| --- |
| VELO hardware interlocks implementation v1.4 LHCb VELO group |
| In this document we specify the VELO hardware interlock implementation Keywords: VELO, interlocks |
| Prepared by : Anthony Smith Univ. of Liverpool Eddy Jans, Luc Jansen, Piet de Groen, Martin van Beuzekom, Ann Van Lysebetten NIKHEF, Amsterdam Lars Eklund Univ. of Glasgow Jan Buytaert, Stefano De Capua CERN | Checked by : VELO group | Approved by : See Distribution Lists below. |
| Distribution Lists: For Approval: T. Bowcock (Univ. of Liverpool), J. Buytaert (CERN), L. Eklund (Univ. of Glasgow), E. Jans (Nikhef, Amsterdam), A. Smith (Univ. of Liverpool), M. van Beuzekom (Nikhef, Amsterdam) For information: R. Lindner (CERN), W. Witzeling (CERN), R. Jacobsson (CERN) |
| Document Status Sheet |
| Version | Date | Pages | Comments or Description of Changes |
| 1.0 1.2 1.3 1.4 | 14-April-2008 28-May-2008 08-Aug-2008 10-Jun-2009 | 11 11 14 | First version First upload for discussion Addition on sections 3 and 4 Corrections |

Table of Contents

1	Introduction	4

2	The VELO hardware interlock unit	5

2.1	Description of the VELO hardware interlock unit	5

2.2	Description of the incoming signals	5

2.3	Description of the outgoing signals	6

2.4	Programming of the FPGA	6

2.5	Testing the unit	7

3	Signals exchanged between the PLCs	8

3.1	Vacuum-Cooling system	8

3.2	Vacuum system - motion	8

4	External Signals	8

4.1	Signal exchange with the LHC vacuum	8

4.2	DSS signal	8

4.3	Signal exchange for the beam dump	8

5	References	10

# Introduction

The VELO hardware interlock system has been developed to protect the VELO against failures during its operation. The functionality of the system is described in details in reference [1]. This document presents the follow-up to the functionality description.

Table 1 gives the overview of all the interlock signals for the VELO. The first group of interlock signals is handled by the VELO interlock hardware unit. “Front-end” stands for all signals coming from the temperature boards. Details on these are given in section 2. The second group of signals is exchanged directly between the PLCs. Section 3 gives an overview of the implementation of these signals. The VELO relies on a few external signals for the interlocks. These are shown in group 3 of table 1; details are given in section 4.

Table 1: Overview of the hardware interlocks for the VELO

|  | Action | From system | Signal | To system | Granularity |
| --- | --- | --- | --- | --- | --- |
| Interlock unit | LV inhibit | Front-end | Warm ok | LV | per LV module |
|  | LV inhibit | Cooling | Cooling ok | LV | per detector half |
|  | LV inhibit | Vacuum | Vacuum ok | LV | full system |
|  | LV inhibit | Front-end | Temp. Board ok | LV | per LV module |
|  | HV inhibit | Vacuum | Vacuum ok | HV | full system |
|  | HV inhibit | Cooling | Cooling ok | HV | per detector half |
|  | HV inhibit | Front-end | Too warm | HV | per ¼ HV module |
|  | HV inhibit | Front-end | Temp. Board ok | HV | Per ¼ HV module |
|  | HV inhibit | LHCb BCM | BCM_OK | HV | full system |
|  | Motion inhibit | LHCb BCM | BCM_OK | Positioning | full system |
|  | Cooling inhibit | Front-end | Cold ok | Cooling | per detector half |
|  | HV inhibit | Emergency button | Em_butt | HV | full system |
|  | LV inhibit | Emergency button | Em_butt | LV | full system |
| PLC | Cooling inhibit | Vacuum | Vacuum ok | Cooling | full system |
|  | Positioning inhibit | Vacuum | Vacuum ok | Positioning | full system |
|  | Venting inhibit | Cooling | Cooling ok | Vacuum | full system |
|  | Vent/evacuate inhibit | Positioning | Motion ok | Vacuum | full system |
| External | Cooling inhibit | Primary water |  | Cooling | full system |
|  | Positioning inhibit | CIBU | MDA/SSB | Positioning | full system |
|  | Beam dump | Positioning | User permit | CIBU |  |
|  | Vent/evacuate inhibit | LHC vacuum sector valves | Sector valves closed | Vacuum | full system |
|  | Venting inhibit | Gas injection | Gas ready | Vacuum | full system |
|  |  |  | Injection valve |  |  |

# The VELO hardware interlock unit

## Description of the VELO hardware interlock unit

The interlocks of the first group in Table 1 are treated in this unit. In this document we only concentrate on the main features and functionality. A more detailed description of this unit can be found in reference [2].

The interlock unit is located in D3E05 (slot 6). A picture is shown in Figure 1.

All the incoming and outgoing signals (see sections 2.2 and 2.3 for further details) have each 2 LEDs on the front panel, a green and an orange LED. For the incoming signals the green LED is lit when the signal present, while the orange is lit when the signal has been forced from the inside. For the outgoing signals the green LED is lit when the signal is not interlocked, the orange is lot when the signal has been forced from the inside. The forcing is done by the override switches inside the box (see reference [3]).

Figure 1: The interlock decision unit.

## Description of the incoming signals

The base granularity in the interlock system comprises 2 VELO modules; this is dictated by the granularity of the too warm signal from the temperature board. For a too warm signal 1 LV module and a ¼ HV module will be switched off. Details on the temperature board can be found in reference [4]. The temperature board triggers 3 types of signals that are sent to the interlock unit:

- “too cold”: one signal per board, or 3 per detector half. The signal is triggered when the temperature given by at least 3 out of 4 NTCs of 1 VELO module is below a too cold threshold. This “too cold” signal is an OR of all 8 modules being too cold per temperature board. For the pile-up….

- “too warm”: 4 signals per temperature board, 1 signal per 2 VELO modules. The signal is triggered when one of the eight NTCs on the 2 VELO modules reads a temperature greater than a too warm threshold.

- Temperature board ok: The signal is high (ok) when the boards are powered and a signal is received by the interlock box. One signal per board is given. This signal is given above the error threshold (see table)

The signals can be masked via PVSS. For this a special masking file needs to be loaded. The masking procedure is explained on the VELO operation wiki pages [5]. Note that masking of crucial parameters will generate an automatic interlock signal:

- If 4 NTCs on one VELO module are masked the interlock is fired. This is 4 maskbits on the too warm levels or 4 maskbits on the error levels. If two NTCs are masked in case of a pile-up module (2 maskbits on the too warm or error levels), an interlock signal is sent as well.

An overview of the different thresholds can be found in table 2. These are approximate values, all values were determined exactly for the different temperature boards [6].

Table 2: Overview of the thresholds for the temperature board interlocks

| Signal | Threshold in V | Threshold in deg C |
| --- | --- | --- |
| error | > 2.451 |  |
| Too cold | > 2.278 | < - 36.9 |
| None, normal operation | 2.278 > > 0.731 | 30.1> >-36.9 |
| Too warm | < 0.731 | > 30.1 |

Besides the spare channel inputs, other incoming signals come from the cooling system, Beam Condition Monitor system, vacuum system and emergency button:

- The Cooling system signals that the cooling has reached a ready state

  - This is defined as the accu setpoint temperature has been reached within 0.5(C and the average cooling cookie temperature stays within a band around this setpoint.

- The Vacuum system delivers a vacuum ok signal

  - This is defined as the pressure is below a level of 10-3 mbar.

- The BCM sends a signal BCM_OK that it is functioning. Essential functionality like HV and programming of the credit card pc is monitored. More information can be found in reference [7].

- The Emergency button:

  - In the LHCb control room an emergency button is installed. In case of communication loss with the D3 environment this can be pushed to switch off all LV and HV channels of the VELO.

Table 3 gives an overview of these signals as seen by the interlock unit. Each temperature board has its own input signals. Spare channels exist.

Table 3: Overview of the input signals to the interlock decision unit

| Input signal | No of signals | From | Signal |
| --- | --- | --- | --- |
| Warm ok 0/1/2/3 | 4 per TB | Temp. Board | Too warm |
| Cold ok | 1 per TB | Temp. Board | Too cold |
| Board ok | 1 per TB | Temp. Board | Temp board ok |
| Cooling ready A/C | 1 per det half | Cooling |  |
| Vacuum ready | 1 | Vacuum |  |
| BCM ok | 1 | BCM |  |
| Emergency button | 1 | Emergency button |  |

## Description of the outgoing signals

The output signals to HV and LV are divided according to the granularity of the temperature boards. Spare channels exist.

Table 4 gives an overview of the outgoing signals.

Table 4: Overview of the output signals from the interlock decision unit

| Output signal | No of signals | To |
| --- | --- | --- |
| CAEN01-11 | 12 | LV |
| A/C_ISEG01/02/03 | 12 | HV |
| Allow CoolingA/C | 2 | Cooling |
| Allow positioning | 1 | Motion |

## Programming of the FPGA

The FPGA in the interlock unit takes the input signals and fires the right output signals taking into account the granularity as described in table 1. The full programming overview can be found in [8]. A correspondence table for the channels affecting each other is found in appendix A.

Below a short overview of the FPGA logic is given:

  - Temperature board fires “too warm” (“warm ok” led goes off)

    - CAEN01-11 leds on front panel will go off and switch off of corresponding LV modules (LV inhibit)

    - A/C_ISEG01/02/03 leds go off and switch off corresponding HV modules (HV inhibit)

  - Temp board fires “too cold” (“cold ok” led goes off):

    - Allow cooling A/C led will go off. If the cooling system runs with the main chiller it will go to backup cooling, if running on backup it will stay running in backup chiller.

    - Note that the “too cold” information of the Temperature boards is ignored by the cooling system when the TB looses the temp board ok signal.

  - Temp board fires not ok (“board ok” led off)

    - CAEN01-11 leds on front panel will go off and switch off of corresponding LV modules (LV inhibit)

    - A/C_ISEG01/02/03 leds go off and switch off corresponding HV modules (HV inhibit)

    - too cold signal is ignored by the cooling system.

  - Vacuum not ready (“vacuum ready” led goes off)

    - CAEN01-11 leds on front panel will go off and switch off of corresponding LV modules (LV inhibit)

    - A/C_ISEG01/02/03 leds go off and switch off corresponding HV modules (HV inhibit)

  - Cooling not ready (“cooling ok A/C” led goes off)

    - CAEN01-11 leds on front panel will go off and switch off of corresponding LV modules (LV inhibit)

    - A/C_ISEG01/02/03 leds go off and switch off corresponding HV modules (HV inhibit)

  - BCM not ok (“BCM ok” LED goes off)

    - A/C_ISEG01/02/03 leds go off and switch off corresponding HV modules (HV inhibit)

    - Allow positioning goes off, detector will retract and is not allowed to move in.

- Emergency button pushed (“Em. butt.” LED goes off)

    - CAEN01-11 leds on front panel will go off and switch off of corresponding LV modules (LV inhibit) for both A and C side

    - ISEG01/02/03 leds go off and switch off corresponding HV modules (HV inhibit) for both A and C side

## Testing the unit

The functionality of the programmed FPGA was tested in the lab standalone and with the input from a temperature board and an output to a CAEN LV module. When installed in D3E05 slot 6, the functionality test was repeated and the different output and input signals were verified. These tests comprised the verification of the signal arrival and its polarity, cross-checking the cabling and channel labeling. The complete chain from VELO repeater boards over the temperature boards down to the LV and HV modules and back was also tested. A first test used a voltage source to mimic the “too warm” and “too cold” signals from the repeater boards to the Temperature Boards. A second test was performed with the dummy module. The LV was switched on for each channel and when the “too warm” threshold was reached it was verified that the interlock had fired. All tests were done in December 2007 and May 2008.

After the uploading of the “final” FPGA firmware and the change of temperature resistors on the temperature boards a full checkout of the system was performed. This was done begin April 2009.

More information on these checkouts can be found in the elog [9, 10]. The full test procedure is described on the VELO operation wiki pages [5]. Testing the interlock decision unit is based on masking 4 NTC channels per VELO module (two for the pile-up) as doing so generates automatically “too warm” signals. This way the functionality of the temperature boards and the interlock decision unit can be checked easily.

# Signals exchanged between the PLCs

## Vacuum-Cooling system

- Cooling inhibit: this interlock signal is sent to the cooling system from the vacuum system. It signals that the detector pressure pdet is larger than a threshold value pcooling (approx. 1e-3 mbar), no neon in the detector or the detector vacuum is unknown (e.g. gauge or control system is off).

- Venting inhibit from the cooling control system. VELO venting can only be done when the cooling does not use the main chiller (SA). While using the back up chiller or when the system is turned off venting is allowed.

## Vacuum - motion system

- Positioning inhibit: this interlock signal is sent to the positioning system and signals that the detector pressure pdet is larger than a threshold value pmotion (approx. 10 mbar) or the detector vacuum is unknown (e.g. gauge or control system is off).

- Vent/evacuate inhibit from the positioning system allows venting and starting evacuation only when the detectors are in the closest position in X relative to each other (software switch at (+2,-2)mm). In this position, the two thin aluminium foils (facing each other) will be spaced by about 4 mm.

The interlock of the vacuum, motion and cooling PLCs can be overruled. For more details see reference manuals on the systems concerned [11, 12].

# External Signals

## Signal exchange with the LHC vacuum

For neon injection this system has to be available. The signal telling whether the neon injection system is available is a logic AND of the following two signals. The VELO vacuum system gets an interlock signal gas ready from the AT-VAC neon gas injection system which will is located in the LHCb cavern. The VELO vacuum system also gets the status of the valve V5 on the injection line.

To allow VELO vacuum procedures the LHC sector valves need to be closed. Therefore the VELO vacuum system also gets two signals from the sector valves.

The LHC vacuum control system provides an interlock signal vent/evacuate inhibit to the VELO vacuum PLC to inhibit VELO venting or starting evacuation when the sector valves are not closed. This interlock signal must be working at all times, even in the case of a power cut (which could be local to the LHC vacuum system and not affecting the LHCb experiment).

## DSS signal

A DSS signal is sent to the cooling PLC when the temperature or flow of the primary cooling water is not ok [13]. In this case the cooling will switch to backup cooling. The status of this signal can be seen in the interlock panel on the cooling PLC (see also reference [13]).

## Signal exchange for the beam dump

The LHC beam interlock system (BIS, see [14]) foresees the possibility for experiments to inhibit beam circulation in the ring. A user permit interlock signal must be provided by the experiment to the closest Beam Interlock Controller (BIC) through the User Interface (CIBU). These signals (coming from all Beam Interlock Controllers) will be then combined in the Beam Interlock System (BIS) and generate a beam permit signal. Whenever user permit is false, the beam permit signal will become false and the beam is dumped (if present) and injection is disabled. There is one such signal per beam. The BIC will allow several potential signal sources within one experiment to be combined into one user permit per beam.

An independent link will allow safe signal exchange between the LHC and the experiments (the Safe LHC Parameters). The states stable beams, unstable beams and adjust correspond to three levels of (increasing) risk associated with their respective allowed beam operations. Entering the adjust state from (un)stable beams requires hand-shaking between the LHC and experiments. Only the two states stable beams and unstable beams are considered safe enough to have the VELO detectors close to the beams (safe beam). An extra state is introduced Movable Devices Allowed (MDA), this is a logic OR of stable and unstable beams. These signals are received from LHC/BIC and by means of the CIBU located in the motion PLC rack.

Via the CIBU the VELO gives back a user permit to LHC/BIC. The user permit signal is set when a logic OR of the following statements is true:

  - |X| > 29 mm ()

  - MDA set and  |X| < 29 mm (3)

Hence when the user permit is not set a beam dump is caused. This implies the following for the VELO motion system (see summary in figure 1):

  - When MDA AND SSB are set

    - VELO can move in/out (situation A)

  - When SSB is lost and  |X|<29 mm (3)

    - VELO will start moving OUT (situation B,C)

    - With eventual timing option and/or button to prevent move out.

Figure 2: Overview of the different situations for the VELO motion system with the LHC parameters.

Open issues:

- To be verified: under which conditions/LHC actions are MDA and SSB set?

- Postmortem publication

  - Via DIP

  - To be verified: format and specifics of the postmortem trigger signal (HW type?)

- Masking of the user permit: VELO will be able to override the user permit in the PLC. This can only be used, password protected in case of VELO failure. Special decision procedure to be defined.

- power of the CIBU on machine UPS?

# References

[1] Velo Hardware interlocks, EDMS document 706629 v2.0

[2] VELO hardware interlock unit, LHCB Technical note, LHCb-2007-0xx, N.A. Smith (to be finalised)

[3] Overview list of the internal switches and connectors, EDMS attachment

[4] Temperature board documentation???? Existing?

[5] https://lbtwiki.cern.ch/bin/view/VELO/VELOOperatingManuals

[6] http://lblogbook.cern.ch/VELO/623

http://lblogbook.cern.ch/VELO/626

[7] BCM manual

[8] Documentation on the programming of the FPGA of the interlock decision unit. (Jan)

[9] http://lblogbook.cern.ch/VELO-installation/131

http://lblogbook.cern.ch/VELO-installation/132

http://lblogbook.cern.ch/VELO-installation/134

http://lblogbook.cern.ch/VELO-installation/144

[10] http://lblogbook.cern.ch/VELO/629

[11] Cooling manual

[12] Vacuum manual

[13] Detector Safety System for the Velo detector, EDMS 830682 V2.0

[14] “The Beam Interlock System fro the LHC”, B. Puccio et al., EDMS Nr. 567256 v0.2, https://edms.cern.ch/document/567256/0.2 .

APPENDIX A: Overview of the signal in and outputs, cable labels. The table gives the correspondence between origin of the signal and its destination.

| Side | Origin | Signal input | Label Cable in | Destination | Signal output | Label Cable out |
| --- | --- | --- | --- | --- | --- | --- |
| A | TB1 | Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling A | Inlk Cool. Cool. Allow A |
|  | TB2 | Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling A | Inlk Cool. Cool. Allow A |
|  | TB3 | Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling A | Inlk Cool. Cool. Allow A |
|  | TB1 | Warm ok 0 | A-side Temp inlk too warm | HV | A_ISEG01 0-3 | A_ISEG 01 0-7 |
|  |  | Warm ok 0 | A-side Temp inlk too warm | LV | CAEN 11 | INLK LV A -CAEN 11 |
|  | TB1 | Warm ok 1 | A-side Temp inlk too warm | HV | A_ISEG01 4-7 | A_ISEG 01 0-7 |
|  |  | Warm ok 1 | A-side Temp inlk too warm | LV | CAEN 01 | INLK LV A- CAEN 01 |
|  | TB1 | Warm ok 2 | A-side Temp inlk too warm | HV | A_ISEG01 8-11 | A_ISEG 01 8-15 |
|  |  | Warm ok 2 | A-side Temp inlk too warm | LV | CAEN 02 | INLK LV A- CAEN 01 |
|  | TB1 | Warm ok 3 | A-side Temp inlk too warm | HV | A_ISEG01 12-15 | A_ISEG 01 8-15 |
|  |  | Warm ok 3 | A-side Temp inlk too warm | LV | CAEN 03 | INLK LV A- CAEN 03 |
|  | TB2 | Warm ok 0 | A-side Temp inlk too warm | HV | A_ISEG02 0-3 | A_ISEG 02 0-7 |
|  |  | Warm ok 0 | A-side Temp inlk too warm | LV | CAEN 04 | INLK LV A- CAEN 04 |
|  | TB2 | Warm ok 1 | A-side Temp inlk too warm | HV | A_ISEG02 4-7 | A_ISEG 02 0-7 |
|  |  | Warm ok 1 | A-side Temp inlk too warm | LV | CAEN 05 | INLK LV A- CAEN 05 |
|  | TB2 | Warm ok 2 | A-side Temp inlk too warm | HV | A_ISEG02 8-11 | A_ISEG 02 8-15 |
|  |  | Warm ok 2 | A-side Temp inlk too warm | LV | CAEN 06 | INLK LV A- CAEN 06 |
|  | TB2 | Warm ok 3 | A-side Temp inlk too warm | HV | A_ISEG02 12-15 | A_ISEG 02 8-15 |
|  |  | Warm ok 3 | A-side Temp inlk too warm | LV | CAEN 07 | INLK LV A- CAEN 07 |
|  | TB3 | Warm ok 0 | A-side Temp inlk too warm | HV | A_ISEG03 0-3 | A_ISEG 03 0-7 |
|  |  | Warm ok 0 | A-side Temp inlk too warm | LV | CAEN 08 | INLK LV A- CAEN 08 |
|  | TB3 | Warm ok 1 | A-side Temp inlk too warm | HV | A_ISEG03 4-7 | A_ISEG 03 0-7 |
|  |  | Warm ok 1 | A-side Temp inlk too warm | LV | CAEN 09 | INLK LV A- CAEN 09 |
|  | TB3 | Warm ok 2 | A-side Temp inlk too warm | HV | A_ISEG03 8-11 | A_ISEG 03 8-15 |
|  |  | Warm ok 2 | A-side Temp inlk too warm | LV | CAEN 10 | INLK LV A- CAEN 10 |
|  | TB3 | Spare | A-side Temp inlk too warm | - | A_ISEG03 12-15 (spare) | - |
|  |  | Spare | A-side Temp inlk too warm | - | CAEN spare | - |
|  | TB1 | Board ok | A+C cold ok Board ok | HV | A_ISEG01 0-15 | A_ISEG 01 0-15 |
|  |  |  |  | LV | CAEN 11-03 | INLK LV A- CAEN 11-03 |
|  | TB2 | Board ok | A+C cold ok Board ok | HV | A_ISEG02 0-15 | A_ISEG 02 0-15 |
|  |  |  |  | LV | CAEN 04-07 | INLK LV A- CAEN 04-07 |
|  | TB3 | Board ok | A+C cold ok Board ok | HV | A_ISEG03 0-15 | A_ISEG 03 0-15 |
|  |  |  |  | LV | CAEN 08-10 + spare | INLK LV A- CAEN 08-10 |
|  | TB1 | Board ok + Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling A | INLK Cool Cool allow A |
|  | TB2 | Board ok + Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling A | INLK Cool Cool allow A |
|  | TB3 | Board ok + Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling A | INLK Cool Cool allow A |
| C | TB1 | Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling C | INLK Cool Cool allow C |
|  | TB2 | Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling C | INLK Cool Cool allow C |
|  | TB3 | Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling C | INLK Cool Cool allow C |
|  | TB1 | Warm ok 0 | C-side Temp inlk too warm | HV | C_ISEG01 0-3 | C_ISEG 01 0-7 |
|  |  | Warm ok 0 | C-side Temp inlk too warm | LV | CAEN 11 | INLK LV C- CAEN 11 |
|  | TB1 | Warm ok 1 | C-side Temp inlk too warm | HV | C_ISEG01 4-7 | C_ISEG 01 0-7 |
|  |  | Warm ok 1 | C-side Temp inlk too warm | LV | CAEN 01 | INLK LV C- CAEN 10 |
|  | TB1 | Warm ok 2 | C-side Temp inlk too warm | HV | C_ISEG01 8-11 | C_ISEG 01 8-15 |
|  |  | Warm ok 2 | C-side Temp inlk too warm | LV | CAEN 02 | INLK LV C- CAEN 02 |
|  | TB1 | Warm ok 3 | C-side Temp inlk too warm | HV | C_ISEG01 12-15 | C_ISEG 01 8-15 |
|  |  | Warm ok 3 | C-side Temp inlk too warm | LV | CAEN 03 | INLK LV C- CAEN 03 |
|  | TB2 | Warm ok 0 | C-side Temp inlk too warm | HV | C_ISEG02 0-3 | C_ISEG 02 0-7 |
|  |  | Warm ok 0 | C-side Temp inlk too warm | LV | CAEN 04 | INLK LV C- CAEN 04 |
|  | TB2 | Warm ok 1 | C-side Temp inlk too warm | HV | C_ISEG02 4-7 | C_ISEG 02 0-7 |
|  |  | Warm ok 1 | C-side Temp inlk too warm | LV | CAEN 05 | INLK LV C- CAEN 05 |
|  | TB2 | Warm ok 2 | C-side Temp inlk too warm | HV | C_ISEG02 8-11 | C_ISEG 02 8-15 |
|  |  | Warm ok 2 | C-side Temp inlk too warm | LV | CAEN 06 | INLK LV C- CAEN 06 |
|  | TB2 | Warm ok 3 | C-side Temp inlk too warm | HV | C_ISEG02 12-15 | C_ISEG 02 8-15 |
|  |  | Warm ok 3 | C-side Temp inlk too warm | LV | CAEN 07 | INLK LV C- CAEN 07 |
|  | TB3 | Warm ok 0 | C-side Temp inlk too warm | HV | C_ISEG03 0-3 | C_ISEG 03 0-7 |
|  |  | Warm ok 0 | C-side Temp inlk too warm | LV | CAEN 08 | INLK LV C- CAEN 08 |
|  | TB3 | Warm ok 1 | C-side Temp inlk too warm | HV | C_ISEG03 4-7 | C_ISEG 03 0-7 |
|  |  | Warm ok 1 | C-side Temp inlk too warm | LV | CAEN 09 | INLK LV C- CAEN 09 |
|  | TB3 | Warm ok 2 | C-side Temp inlk too warm | HV | C_ISEG03 8-11 | C_ISEG 03 8-15 |
|  |  | Warm ok 2 | C-side Temp inlk too warm | LV | CAEN 10 | INLK LV C- CAEN 10 |
|  | TB3 | Spare | C-side Temp inlk too warm | - | C_ISEG03 12-15 (spare) | - |
|  |  | Spare | C-side Temp inlk too warm | - | CAEN spare | - |
|  | TB1 | Board ok | A+C cold ok Board ok | HV | C_ISEG01 0-15 | C_ISEG 01 0-15 |
|  |  |  |  | LV | CAEN 11-03 | INLK LV C- CAEN 11-03 |
|  | TB2 | Board ok | A+C cold ok Board ok | HV | C_ISEG02 0-15 | C_ISEG 02 0-15 |
|  |  |  |  | LV | CAEN 04-07 | INLK LV C- CAEN 04-07 |
|  | TB3 | Board ok | A+C cold ok Board ok | HV | C_ISEG03 0-15 | C_ISEG 03 0-15 |
|  |  |  |  | LV | CAEN 08-10 + spare | INLK LV C- CAEN 08-10 |
|  | TB1 | Board ok + Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling C | INLK Cool Cool allow C |
|  | TB2 | Board ok + Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling C | INLK Cool Cool allow C |
|  | TB3 | Board ok + Cold ok | A+C cold ok Board ok | Cooling PLC | Allow Cooling C | INLK Cool Cool allow C |
| A | Cool. PLC | Cooling ready A | Intlk cool. Cool. Ready A | HV | A_ISEG01-02-03 | A_ISEG 01-03 0-15 |
|  |  |  |  | LV | A_CAEN 0-11 | INLK LV A- CAEN 0-11 |
| C |  | Cooling ready C | Intlk cool. Cool. Ready C | HV | C_ISEG01-02-03 | C_ISEG 01-03 0-15 |
|  |  |  |  | LV | C_CAEN 0-11 | INLK LV C- CAEN 0-11 |
| A/C | Vac. PLC | Vacuum ready | Intlk vac. vac. Ready | HV | A_ISEG01-02-03 C_ISEG01-02-03 | A_ISEG 01-03 0-15 C_ISEG 01-03 0-15 |
|  |  |  |  | LV | A_CAEN 0-11 C_CAEN 0-11 | INLK LV A- CAEN 0-11 INLK LV C- CAEN 0-11 |
|  | BCM | BCM ok | Intlk BCM BCM OK | Motion PLC | Allow close | INLK MOT Det out |
|  |  |  |  | HV | A_ISEG01-02-03 C_ISEG01-02-03 | A_ISEG 01-03 0-15 C_ISEG 01-03 0-15 |
|  | Emergency button | Em. Butt. | Inlk. EM. Butt. | LV | A_CAEN 0-11 C_CAEN 0-11 | INLK LV A- CAEN 0-11 INLK LV C- CAEN 0-11 |
|  |  |  |  | HV | A_ISEG01-02-03 C_ISEG01-02-03 | A_ISEG 01-03 0-15 C_ISEG 01-03 0-15 |

# Footnotes

Vacuum ready can be forced from the PLC, see vacuum operation manual

Cooling ready can be forced from the PLC, see cooling operation manual

|X| is defined as the (|X_A| OR |X_C|)

# Text boxes

MDA

Velo movement

SSB

MDA

Velo movement

SSB

MDA

out

out

out

in

Beam DUMP

(C)

(B)

(A)

Velo movement

SSB