## Slide 1: SOME THERMODYNAMIC RELATIONS
HEAT TRANSFER
Conduction Q = kA dt/dx k is the thermal conductivity
Convection
Radiation P = esT4 per unit area. e is the emissivity, s is the Stefan-Boltzmann constant
= 5.67 10-8 W m-2 K-4
1st Law DU = dQ – dW For fluids dW = pdV
Entropy Ds = DQREV / T
Efficiency of a Carnot Engine hC = 1 – T2 / T1
Enthalpy h = u + pv Useful for describing
1. Heat transfer at constant pressure in a boiler or
condenser. Heat input Q = h2 - h1 (2.1)
2. Adiabatic changes in compressors and turbines where
net work on the shaft W = h1 - h2 (2.2)
(See derivation 2.2 in the text book for proof of these last two relations)

## Slide 2: THE GREENHOUSE EFFECT
Solar radiation incident on Earth has an intensity S = 1.37 kW m-2
  Energy spectrum from IR to UV. Assume the atmosphere is almost transparent to solar radiation but absorbs radiation from Earth (IR)
A fraction of solar radiation, the albedo, A, is reflected by clouds and the Earth’s surface back into space (this is close to 30%)
  (1-A)S heats up the earth
  to a temperature Te which
  radiates Se (IR) outwards
  Water vapour + CO2 + …
  absorb IR
  The temperature of the
  atmosphere is Ta which
  then radiates a flux Sa
  both upwards and out
  into space

## Slide 3
If there was no atmosphere the total heat absorbed by the Earth would be (1-A).Sp R2 (R is the radius of the Earth)
Equilibrium would be reached at a temperature T where
(1-A).Sp R2 = 4p R2 sT4 (assuming e = 1) (2.3)
Putting A = 0.3 gives T = 255 K
Taking e = 1 for the atmosphere with temperature Ta we have the net heat absorbed being radiated out into space by the atmosphere
(1-A).Sp R2 = 4p R2 sTa4 (2.4)
But the surface now receives extra heat from the atmosphere and so reaches a temperature Te where
(1-A).Sp R2 + 4p R2 sTa4 = 4p R2 sTe4 (2.5)
From these equations we obtain Te4 = 2T4
So Te = 303K
More realistically we should account for the small fraction f of solar radiation absorbed by the atmosphere adding a factor (1-f) to the first term in (2.5)

## Slide 4: CLOSED CYCLE FOR STEAM POWER PLANT
The working fluid undergoes changes of phase in a closed cycle
Compressor
  Work Wcom done on system to compress cold water from sub-atmospheric pressure to high pressure
Boiler
  Heat Q1 added to convert cold water to steam
Turbine
  Work Wt done by system
  (i.e. by steam) on
  turbine blades
Condenser
  Heat Q2 lost from system
  to environment
  ( steamcold water)

## Slide 5: -
1st Law
After each complete cycle DU = 0 = (Q1-Q2)-(Wt-Wcom)=0 1st Law
Efficiency h = net work out / heat in = (Wt-Wcom)/Q1 = (Q1-Q2)/Q1
 h = 1 - Q2 / Q1 (2.6)
The maximum efficiency is limited by the 2nd Law of Thermodynamics.
The Carnot cycle for a perfect gas
involves reversible isothermal and
adiabatic changes leading to
hC = 1 - T2 / T1 (2.7)

## Slide 6: THERMAL PROPERTIES OF WATER AND STEAM
3 regions of interest
  Water
  Mixture of water + steam
  Dry steam
T – s diagram
Solid blue lines are isobars
Dotted lines have constant x
For a mixture Steam Quality x = mgas / m where m = mgas + mfluid
Steam tables give specific values of s, u and h for fluid and gas
from which the value for a mixture can be determined
  eg . mh = mgas hgas + mfluid hfluid
  h= (1-x) hfluid + x hgas per unit mass (2.80)
The path ABCD corresponds to water boiling and becoming dry steam

## Slide 7: Example:- A steam power plant operates on a Carnot cycle. The boiler is at T1=352oC, p=170 bar and the condenser is at T2 = 30oC, p = 0.04 bar
 |  | h (kJ kg-1) |  | s (kJ kg-1 K-1) | 
T(oC) | P (bar) | hfluid | hgas | sfluid | sgas
30 | 0.04 | 126 | 2556 | 0.436 | 8.452
352 | 170 | 1690 | 2548 | 3.808 | 5.181
hC = 1 - T2 / T1 = 1-303/625 ~ 0.52
Since the boiler is at constant pressure
Q1 = hb-ha = 2548-1690 = 858 kJ kg-1
Since bc is adiabatic in the Carnot cycle Wt = hb – hc=2548 – hc
To find hc we use hc = (1-xc) hfluid + xc hgas where xc is value of x at c
To find xc note that sb=sc = 5.181 (adiabatic expansion in the turbine)
But sc = (1-xc) sfluid + xcsgas = (1-xc) 0.436 + 8.452xc = 5.181
Hence xc = 0.59 and so hc = (1-0.59)x126 + 0.59 x 2556 = 1560 kJ kg-1
So work done by the turbine Wt = hb – hc=2548 – 1560 = 988 kJ kg-1
A similar analysis to find xd gives xd = 0.42 and Q2 = hc-hd = 413kJ kg-1

## Slide 8: RANKINE CYCLE
The Carnot cycle is impractical using water as the working fluid
  Need T1 constant. Only possible in region II
  Region II is 2 phase. Fast water droplets damage turbine blades
  and compressor blades
  Volume of steam is very large – expensive compressor
In the Rankine cycle all the steam is converted
to water (de) before entering the compressor
which raises the pressure adiabatically (ef)
Modern plants have 3 sections
Economiser heats water until boiling (fa)
Evaporator converts water to dry steam (ab)
Superheater heats dry steam at constant p (bc).
Work on turbine blades (cd) then wet steam enters the condenser.
Typical efficiencies with reheat are in the range 40 – 45%
Tc is limited to 650 oC to avoid corrosion
The Carnot cycle is impractical using water as the working fluid
  Need T1 constant. Only possible in region II
  Region II is 2 phase. Fast water droplets damage turbine blades
  and compressor blades
  Volume of steam is very large – expensive compressor
In the Rankine cycle all the steam is converted
to water (de) before entering the compressor
which raises the pressure adiabatically (ef)
Modern plants have 3 sections
Economiser heats water until boiling (fa)
Evaporator converts water to dry steam (ab)
Superheater heats dry steam at constant p (bc).
Work on turbine blades (cd) then wet steam enters the condenser.
Typical efficiencies with reheat are in the range 40 – 45%
Tc is limited to 650 oC to avoid corrosion
The Carnot cycle is impractical using water as the working fluid
  Need T1 constant. Only possible in region II
  Region II is 2 phase. Fast water droplets damage turbine blades
  and compressor blades
  Volume of steam is very large – expensive compressor
In the Rankine cycle all the steam is converted
to water (de) before entering the compressor
which raises the pressure adiabatically (ef)
Modern plants have 3 sections
Economiser heats water until boiling (fa)
Evaporator converts water to dry steam (ab)
Superheater heats dry steam at constant p (bc).
Work on turbine blades (cd) then wet steam enters the condenser.
Typical efficiencies with reheat are in the range 40 – 45%
Tc is limited to 650 oC to avoid corrosion

## Slide 9: GAS TURBINES AND THE BRAYTON CYCLE
In a gas turbine the products of combustion are typically ~ 1300oC
Gas turbines operate in the Brayton (or Joule) cycle
Air at 1 bar (a) is compressed to 10 – 20 bar (b)
It is then mixed with fuel and the exhaust gases enter the turbine (c)
And vented at (d) to the atmosphere
Adiabatic process in the compressor so Wcom= hb – ha
Similarly in the turbine Wt= hc - hd
Heat supplied Q1 = hc- hb= cp(Tc - Tb) and
Heat rejected Q2 = hd- ha= cp(Td - Ta)
where cp is the specific heat capacity at constant pressure

## Slide 10
Efficiency h = (Q1 – Q2) / Q1 = [(Tc-Tb) - (Td-Ta)] / (Tc-Tb)
Since PVg = constant and PV=RT we have P(1-g) Tg = constant so
Efficiencies for simple gas turbines ~ 40%
This can be improved by combining the
Brayton and Rankine cycles to make a
Combined Cycle Gas Turbine (CCGT)
Efficiencies ~ 60%
Combined Heat and Power cycle (CHP)
uses waste heat for district heating
Efficiencies ~80% but expensive

## Slide 11: GEOTHERMAL ENERGY
An Aquifer is a layer of porous rock trapped between layers of impermeable rock
Heat is extracted by pumping water at
temperature T0 down a borehole and
extracting water at T1 at a 2nd borehole
Heat available per unit volume of rock is
rrcr(T1-T0)
Assume the aquifer has cross- sectional area
A & porosity f (fraction of volume occupied by pores)
Power output for a volume flow Q= A vw is P=rwcw(T1-T0)Q (2.9)
A ‘cold front’ moves through with speed vf. In time dt volume of rock exposed = (1-f)A vf dt and heat removed = heat gained by water
 rrcr(T1-T0) (1-f)A vf dt = rwcw(T1-T0) A vw dt
So vf =l vw where l = rwcw / rrcr(1-f) (2.10)
The lifetime = time for cold front to reach outlet tlife= L / vf (2.11)
Total energy available is fixed E= rrcr(T1-T0) AL (2.12)
so the choice of Q (vw) and tlife are determined by economics

## Slide 12
Flow rate is determined by Darcy’s Law Q = kA Dp / L (2.13) where k is the permeability of the rock and Dp the pressure difference
Other techniques can be used:-
Heat can be extracted from hot dry rocks at higher temperatures
Heat pumps are also used for heating and cooling
  In US over 40% energy and nearly 40% CO2 emissions are from water heating, space heating and cooling
  100,000 geothermal heat pumps are estimated to save 1.1 106 tonnes of carbon over a 20 year period
Drilling for geothermal power is speculative but it is a largely untapped source
  Currently ~ 1TW is extracted world wide
  Potential to provide 5% of global electricity by 2020